## Slide 1: EN 410 Energy Management
Gurubalan Annadurai
guru.a@iitb.ac.in

## Slide 2: Pump performance parameters

## Slide 3: Pump selection curve

## Slide 4: Effect of oversized pump
What happened if we select A instead of E?
Pump cost of E is INR 300000
Operating hours = 8000 hrs./year
Utility rate = INR 5.5/kWh
Motor efficiency = 90%
Density of water = 1000 kg/m3

## Slide 5: Pump Control Strategies
Often Oversizing – Does not operate at Design point
Bypass Control
Throttling
Variable Speed Drives
Trimming Impeller (reducing Diameter)

## Slide 6: Bypass control
Pump runs continuously at the maximum process demand level, with a permanent bypass line attached to the outlet.
When a lower flow is required, the surplus liquid is bypassed and returned to the supply source.

## Slide 7: Valve control method

## Slide 8: The Affinity Laws

## Slide 9: Impeller trimming to reduce flow
Permanent changes
Impeller diameters are rarely reduced below 70% of their original size

## Slide 10: Pump speed adjustments
Multiple-speed pump motors and variable speed drives (VSDs)
Multiple-speed motors: different set of windings for each motor speed
  Expensive, less efficient, discrete speeds
Mechanical VSDs: hydraulic clutches, fluid couplings, and adjustable belts and pulleys.
Electrical VSDs: eddy current clutches, wound-rotor motor controllers, and variable frequency drives (VFDs)

## Slide 11: Speed control
A centrifugal pump, pumping water operates at 35 m3/h and at 1440 RPM. The pump operating efficiency is 68% and motor efficiency is 90%. The discharge pressure gauge shows 4.4 kg/cm2. The suction is 2 m below the pump centerline. If the speed of the pump is reduced by 50% estimate the new flow, head and power.
Original Modified
  flow:
  head:
  power:

## Slide 12: Speed control
A centrifugal pump, pumping water operates at 35 m3/h and at 1440 RPM. The pump operating efficiency is 68% and motor efficiency is 90%. The discharge pressure gauge shows 4.4 kg/cm2. The suction is 2 m below the pump centerline. If the speed of the pump is reduced by 50% estimate the new flow, head and power.
Original Modified
  flow: 35 m3/h 17.5 m3/h
  head: 46 m 11.5 m
  power: 7.17 kW 0.9 kW

## Slide 13: Speed Control

## Slide 14: Pumps in Series/Parallel

## Slide 15: Symptoms for energy efficient operation

## Slide 16: Piping arrangements

## Slide 17: References
https://www.energy.gov/sites/prod/files/G_Overview_of_Pump_Systems_Matter.pdf
https://blog.craneengineering.net/pumps-dont-suck-and-other-centrifugal-pump-basics
https://marinersgalaxy.com/what-is-reciprocating-pump-and-how-i/
https://pumpsdesign.com/system-characteristic-curve/
https://www.springerpumps.com/productnews/npsh-net-positive-suction-head-matters/
https://www.energy.gov/sites/prod/files/2014/05/f16/pump.pdf
https://actamont.tuke.sk/pdf/2018/n2/3qazizada.pdf