## Slide 1: EN 410 Energy Management
Gurubalan Annadurai
guru.a@iitb.ac.in

## Slide 2: Psychometric process
How do estimate the energy transfer in each process
B and F are the major air conditioning process

## Slide 3: Summer Air Conditioning System
Sensible Load
Latent Load

## Slide 4: Cooling and Dehumidification
Outdoor condition is 35℃, 50% RH
Indoor condition is 24℃, 50% RH
How to design your air conditioning system?

## Slide 5: Vapor Compression Refrigeration system
A ton of refrigeration (1 TR) is defined as the amount of heat, which is to be extracted from one tonne of water at 0℃ in order to convert into ice at 0℃ in 24 hours (1 day).
1 TR = 210 kJ/min = 3.5 kW.

## Slide 6: Refrigerants
REFRIGERANT | TYPE | ODP* | GWP*
R-12 | CFC | 0.820 | 10,600
R-22 | HCFC | 0.034 | 1,700
R-404A | HFC | 0 | 3,800
R-410A | HFC | 0 | 2,000
R-134a | HFC | 0 | 1,300
R-290 (Propane) | Natural | 0 | ~20
R-717 (Ammonia) | Natural | 0 | <1
R-1234yf | Unsaturated HFC | 0 | 4

## Slide 7: Estimate the energy demand (EER) of an air-conditioner
Inlet condition: DBT=20℃, WBT=14℃
Outlet condition: DBT=12.7℃, WBT=11.3℃
Capacity = 10 TR
Air flow rate = 4751 m3/hr
Power consumption = 4300 W

## Slide 8: Strategies of Net Zero Buildings - Space Cooling
Reduce the room load
Reduce the system load
Meet the load by passive cooling methods

## Slide 9
Insulation
Reasons to provide insulation.
Thermal Protection
Roof Load Distribution
Building Codes and Standards (IS 3792-1978)
Types of Wall Insulation Materials
  Fiberglass
  Mineral wool
  Cellulose
  Natural fibers
  Polystyrene
  Insulation facings
  Polyisocyanurate
  Polyurethane
  Perlite
  Cementitious foam
  Phenolic foam
Reduce the room load

## Slide 10
Green Roof
Green roof or living roof or Eco roof is a roof which is partially or completely covered with vegetation and a growing medium, planted over a waterproofing membrane.
  Single Course Extensive
  Multi- Course Extensive
  Semi Intensive
  Intensive
Types of green roof systems
Reduce the room load

## Slide 11
Cool Roof
Cool roofs are the roofs that can deliver high solar reflectance and high thermal emittance
  Acrylic based cool coats
  Spray polyurethane cool coats
  Polymer cool coats
  Fiber Filled liquid cool coats
Coatings Types
Reduce the room load

## Slide 12
Phase Change Material
PCMs absorb and release heat, stabilizing indoor temperatures
Benefits include energy savings, improved comfort, and reduced emissions
Reduce the room load

## Slide 13
Double-Paned/Glazed Window
A double-paned window has two panes of glass set into a frame. Between the glass is an intervening gas or air pocket to better insulate a room.
Reduce the room load

## Slide 14
Shading
Reduce the room load

## Slide 15: Economizer
Reduce the system load

## Slide 16: Energy Recovery Ventilator
Reduce the system load

## Slide 17: Cold Storage
Reduce the system load

## Slide 18: Radiant cooling system
Reduce the system load

## Slide 19: Evaporative cooling
Passive cooling

## Slide 20
Heat Exchanger
Absorber
Thermal Compression
VCRS
Thermal
Power
Plant
Vapor absorption system
Working Pairs:
LiBr – H2O ,
NH3 – H2O,
R134a - DMAC
Passive cooling

## Slide 21
Expected losses in power lines
Power plant loss : 70%
(Efficiency = 30%)
Generator Loss : 5%
T &D Loss : 30%
End Equipment loss : 10%
25 kW – 7.5 kW – 6.75 kW – 4.75 kW – 4.25 kW
Heat Source to Site Power Factor: 4.25/25 = 0.17
Power generation – Transmission – Compression Cooling
Vapor absorption system
Passive cooling

## Slide 22
Liquid desiccant cooling system
Passive cooling

## Slide 23
Solid desiccant cooling system
Passive cooling

## Slide 24: Geothermal cooling
Passive cooling

## Slide 25
Deep Sea Water Cooling System
Passive cooling

## Slide 26
Trombe wall / Solar chimney
Ventilation cooling

## Slide 27: Wind tower
Ventilation cooling

## Slide 28: References
https://www.trane.com/content/dam/Trane/Commercial/global/products-systems/education-training/engineers-newsletters/airside-design/admapn020en-0406.pdf
https://nzeb.in/knowledge-centre/hvac-2/radiant-cooling-systems/
NPTEL, Mechanical Engineering - Refrigeration and Air Conditioning
https://archive.nptel.ac.in/courses/112/105/112105129/
Karthik Panchabikesan, Kumaresan Vellaisamy, Velraj Ramalingam, Passive cooling potential in buildings under various climatic conditions in India, Renewable and Sustainable Energy Reviews, Volume 78, 2017, Pages 1236-1252,
https://climate.earthathome.org/sunlight-stored-in-soil/
https://fairconditioning.org/knowledge/passive-design/shading/
https://www.sciencedirect.com/science/article/pii/S1364032116002665#f0010