## Slide 1: EN 410 Energy Management
Gurubalan Annadurai
guru.a@iitm.ac.in

## Slide 2: Heat Exchanger
A heat exchanger is a device which allows transfer of heat energy from one fluid to another fluid, generally without mixing.
To get fluid streams to the right temperature for the next process (reactions often require feeds at high temp)
To condense vapours
To evaporate liquids
To recover heat to use elsewhere
To reject low-grade heat
To drive a power cycle

## Slide 3: Types according to flow
Multi-pass requirement
Header arrangement
Pumping power
Both at almost same exit temperature
Moderate wall temperature
Best performance (later proved based on LMTD)

## Slide 4: Multipass arrangement

## Slide 5: Types by construction – Double pipe HX
Simplest type has one tube inside another
Normal size - 0.25 to 200 m2
Multiple units are often used
Advantages
  Easy to obtain counter-current flow
  Can handle high pressure
  Easy to maintain and repair
  Modular construction
Disadvantage
  Become expensive for large duties (above 1 MW)

## Slide 6: Shell and tube HX
Size per unit - 10 - 1000 m2
Easy to build multiple units
Advantages
  Extremely flexible and robust design
  Easy to maintain and repair
  Can be designed to be dismantled for cleaning
  Many suppliers
Disadvantages
  Require large plot (footprint) area - often need extra space to remove the bundle
  Flow-induced vibrations, noise, thermal stresses, and entry impingement problems

## Slide 7: Scope of shell and tube HX
Maximum pressure
  300 bar (abs) on shell side
  1400 bar (abs) on tube side
Temperature range
  -100 to 600oC (-150 to 1100oF)
  possibly wider with special materials
Fluid limitations
  Few since can be built of many metals

## Slide 8: Allocation of Fluids
Put dirty stream on the tube side - easier to clean inside the tubes
Put high pressure stream in the tubes to avoid thick, expensive shell
When special materials required for one stream, put that one in the tubes to avoid expensive shell
Cross flow gives higher coefficients than in plane tubes, hence put fluid with lowest coefficient on the shell side

## Slide 9: Plate HX
“Plate exchanger” normally refers to a gasketed plate- and-frame exchanger
Advantages
High heat transfer coefficients
Even distribution of heat transfer no hot/cold spot
Contains small amount of fluid which is useful for quick transient
Low pressure drop
Easy cleaning
Disadvantages
Due to gasket issue, not favourable for high vacuum, erosive duties
Relatively low pressure capability

## Slide 10: Extended surface heat exchangers
High effectiveness is needed (>98%)
Compactness > 700m2/m3
High pressure drop

## Slide 11: Compactness
Can be measured by the heat-transfer area per unit volume or by channel size
Conventional exchangers (shell and tube) have channel size of 10 to 30 mm giving about 100 m2/m3
Plate-type exchangers have typically 5 mm channel size with more than 200 m2/m3
More compact types available

## Slide 12: Heat Exchanger Analysis
i – enthalpy
T – Temperature
m – mass flow rate
Cp – specific heat capacity
Q – Heat transfer

## Slide 13: Overall heat transfer coefficient, U (W/m2C)
For plate type
For tubular type

## Slide 14: LMTD Method for Heat Exchanger Analysis

## Slide 15: Analysis for other flow arrangement
F – Correction factor

## Slide 16: Procedure for selecting heat exchanger
With the LMTD method, the task is to select a heat exchanger that will meet the prescribed heat transfer requirements. The procedure for the selection process is
Select the type of heat exchanger suitable for the application.
Determine any unknown inlet or outlet temperature and the heat transfer rate using an energy balance.
Calculate the log mean temperature difference Tlm and the correction factor F, if necessary.
Obtain (select or calculate) the value of the overall heat transfer coefficient U.
Calculate the heat transfer surface area As .
The task is completed by selecting a heat exchanger that has a heat transfer surface area equal to or larger than As.

## Slide 17: Effectiveness–NTU method
A second kind of problem encountered in heat exchanger analysis is the determination of the heat transfer rate and the outlet temperatures of the hot and cold fluids for prescribed fluid mass flow rates and inlet temperatures when the type and size of the heat exchanger are specified.

## Slide 18: Effectiveness

## Slide 19: Effectiveness–NTU method
For specified values of U and Cmin, the value of NTU is a measure of the surface area As. Thus, the larger the NTU, the larger the heat exchanger.
Capacity ratio

## Slide 20: Effectiveness–NTU method
ε increases with increasing values of NTU for a specified C*
ε increases with decreasing values of C* for a specified NTU
For ε < 40%, the capacity rate ratio C* does not have a significant influence on ε
When C* =0?

## Slide 21: Fouling
Fouling is general term that includes any kind of deposits that appears on the heat exchanger surface over the lifetime of the exchanger.
It introduces an additional resistance to heat transfer
Sometimes the deposit is heavy enough to interfere with the flow and increase the pressure drop
Keeping velocities sufficiently high to avoid deposits
Avoiding stagnant regions where dirt will collect
Avoiding hot spots where coking or scaling might occur
Avoiding cold spots where liquids might freeze or where corrosive products may condense from gases

## Slide 22: Selection of HX
The proper selection of a heat exchanger depends on several factors:
Heat Transfer Rate
Cost
Pumping Power
Size and Weight
Type
Materials

## Slide 23: Waste heat recovery options
The waste heat of hot exhaust gases from a heat treating furnace at 427℃ with a flow rate of 1.72 kg/s. The minimum allowable exit temperature is 204℃. Specific heat is 1.05 kJ/kg.K. The furnace burns coal whose heating value is 26749 kJ/kg with an air fuel ratio of 20, and has an efficiency of 75%. There are two options
Preheat the combustion air entering the furnace at 27℃ (U = 23 W/m2K)
Generate steam at 8 bar (2770 kJ/kg )at the rate of 0.136 kg/s. Liquid water enters the waste heat boiler at 116℃ (485 kJ/kg ). U is 142 W/M2k
Calculate the fuel savings, and required surface area and effectiveness of the heat exchanger for both options.

## Slide 24: References
Heat Exchangers - Selection, Rating, and Thermal Design
By Sadik Kakaç, Hongtan Liu, Anchasa Pramuanjaroenkij
Heat And Mass Transfer Fundamentals And Applications
by Yunus A. Cengel and Afshin G. Ghajar